## HTD Template Information
Version | V1.3
Mandatory: All the cells in Column C in yellow have to be completed mandatorily.
Optional: The cells in blue are for multiple objects, that can be completed when needed.

## Test Case
Test Case | Instructions are provided as comments in the rows
ID
Name of the Test Case
Version management
Author
Version
Project
Date
Narrative
Description
Diagram reference
Function(s) under Investigation (FuI)
Description
Diagram reference
Object under Investigation (OuI)
Description
Diagram reference
Domain under Investigation (DuI)
Description
Diagram reference
Purpose of Investigation (PoI)
Description
Diagram reference
System under Test (SuT)
Description
Diagram reference
Functions under Test (FuT)
Description
Diagram reference
Test criteria (TCR)
Target Metrics (TM)
Variability Attributes (VA)
Quality Attributes (QA)
Qualification Strategy
Description
Diagram reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Test Specification
Test Specification | Instructions are provided as comments in the rows
ID
Reference to Test Case
Title of Test
Test Rationale
Description
Diagram Reference
Specific Test System
Description
Diagram Reference
Target measures
Input and output parameters
Test Design
Description
Diagram Reference
Initial system state
Evolution of system state and test signals
Other parameters
Temporal resolution
Source of uncertainty
Suspension criteria / Stopping criteria
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Experiment Specification
Experiment Specification | Instructions are provided as comments in the rows
ID
Reference to Test Specification
Title of Experiment
Research Infrastructure
Description
Diagram Reference
Experiment Realisation
Description
Diagram Reference
Experiment Setup
Description
Diagram Reference
Experimental Design and Justification
Description
Diagram Reference
Precision of equipment and measurement uncertainty
Storage of experiment data
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## 02
Test Case | Instructions are provided as comments in the rows
| ID | 02
| Name of the Test Case | Complying with the fault-ride-through (FRT) requirements in inverter-based droop-controlled microgrids
Version management
| Author | Alexandros G.Paspatis, Alkistis Kontou
| Version | 2
| Project | ERIGRID 2.0
| Date | 13/04/2020
Narrative
| Description | An inverter-based microgrid is considered, with inverter-interfaced distributed energy resources (DERs) operating in parallel to feed the microgrid load. At some point, a network fault occurs, either inside the microgrid (when considering an islanded microgrid) or at the main grid (when considering a grid-connected microgrid). Through the control design of the inverter-interfaced distributed energy resources, power sharing is achieved between the multiple inverters during normal grid conditions. In this way, all inverters are equally stressed while the voltage and frequency of the microgrid are regulated close to their nominal values (droop control operation). Furthermore, when the network fault occurs, the inverters inject power according to the international standards to provide grid voltage support.
Diagram reference
Function(s) under Investigation (FuI)
| Description | Power sharing in inverter-based microgrids and grid voltage support from inverters, during grid faults
Diagram reference
Object under Investigation (OuI)
| Description | Inverter-interfaced distributed energy resources controllers
Diagram reference
Domain under Investigation (DuI)
| Description | Electrical Power
Diagram reference
Purpose of Investigation (PoI)
| Description | - Transition to future smart-grids, where inverter-interfaced DERs provide multiple ancillary services - Characterization and validation of the SuT - Verification and validation of the OuI - Verification and validation of the FuT
Diagram reference
System under Test (SuT)
| Description | An inverter-based microgrid consisting of multiple inverter-interfaced distributed energy resources (DERs), lines, loads, etc.
Diagram reference
Functions under Test (FuT)
| Description | A unified inverter controller that incorporates droop control and fault-ride-through techniques.
Diagram reference
| Test criteria (TCR) | Microgrid operation according to the designed control algorithm
| Target Metrics (TM) | 1. Is power sharing achieved according to the droop control technique? 1. Is voltage support provided to the grid when grid faults occur according to the international standards?
| Variability Attributes (VA) | 1. Different microgrid loading 1. Different grid faults
| Quality Attributes (QA) | 1. During the normal operation, the acceptable load voltages values should be inside the ±5% of the nominal voltage and the acceptable frequency values should be inside ±1% of the nominal frequency 1. Reactive power injection during grid faults, as a percentage of Smax 1. Inverter currents below their maximum threshold Imax
Qualification Strategy
| Description | The major ancillary services required from inverter-interfaced DERs during i) normal operation (droop control) and ii) during grid faulty operation (fault-ride-through) will be investigated through a single test where the inverters are equipped with the appropriate smart control algorithms.
Diagram reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## 02.01
Test Specification | Instructions are provided as comments in the rows
| ID | 02.01
| Reference to Test Case | 02
| Title of Test | Complying with the fault-ride-through (FRT) requirements while maintaining power sharing
Test Rationale
| Description | N/A
Diagram Reference
Specific Test System
| Description | Laboratory setup
| Diagram Reference | Lab_setup.png
| Target measures | Inverter power injection, load voltage and frequency, inverter currents
| Input and output parameters | Input: - Load - Inverter power injection set-points - Grid conditions Output: - Power, voltage, current and frequency measurements
Test Design
| Description | 1. Operate multiple inverters in parallel 1. Perform a network fault when the microgrid operates either in islanded (non-interconnected) mode or in grid-connected mode 1. Save the experimental results
Diagram Reference
| Initial system state | - Inverter controllers enabled - Hardware or simulated network and devices up and running - Computer displaying and saving data
| Evolution of system state and test signals | The system goes from normal operation (operation close to nominal voltage and frequency) to operation under grid faults, to test the inverter control algorithms
| Other parameters | N/A
| Temporal resolution | N/A
| Source of uncertainty | Impedance of load and lines, inverter sensors operation
| Suspension criteria / Stopping criteria | Abnormal current/ power injections from inverters
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
| Diagram id | image1.png
| Diagram name | image1.png
| Diagram URI type | image
| Diagram URI value | image1.png

## 02.01.01
Experiment Specification | Instructions are provided as comments in the rows
| ID | 02.01.01
| Reference to Test Specification | 02.01
| Title of Experiment | Hardware-in-the-Loop for inverter controller validation in real conditions
Research Infrastructure
| Description | Electric Energy Systems (ICCS-NTUA)
Diagram Reference
Experiment Realisation
| Description | Multiple inverters forming a microgrid, both through hardware setup and through simulated components in the RTDS
Diagram Reference
Experiment Setup
| Description | 1. Real Time Digital Simulator (RTDS) 1. PC for RSCAD (UI of RTDS) 1. Hardware controller (Triphase) 1. Interfacing I/O cards
Diagram Reference
Experimental Design and Justification
Description
Diagram Reference
| Precision of equipment and measurement uncertainty | Software real-time measurements from RTDS, 50μs simulation step
| Storage of experiment data | Matlab files and Excel files
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value