## HTD Template Information
Version | V1.3
Mandatory: All the cells in Column C in yellow have to be completed mandatorily.
Optional: The cells in blue are for multiple objects, that can be completed when needed.

## Test Case
Test Case | Instructions are provided as comments in the rows
ID
Name of the Test Case
Version management
Author
Version
Project
Date
Narrative
Description
Diagram reference
Function(s) under Investigation (FuI)
Description
Diagram reference
Object under Investigation (OuI)
Description
Diagram reference
Domain under Investigation (DuI)
Description
Diagram reference
Purpose of Investigation (PoI)
Description
Diagram reference
System under Test (SuT)
Description
Diagram reference
Functions under Test (FuT)
Description
Diagram reference
Test criteria (TCR)
Target Metrics (TM)
Variability Attributes (VA)
Quality Attributes (QA)
Qualification Strategy
Description
Diagram reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Test Specification
Test Specification | Instructions are provided as comments in the rows
ID
Reference to Test Case
Title of Test
Test Rationale
Description
Diagram Reference
Specific Test System
Description
Diagram Reference
Target measures
Input and output parameters
Test Design
Description
Diagram Reference
Initial system state
Evolution of system state and test signals
Other parameters
Temporal resolution
Source of uncertainty
Suspension criteria / Stopping criteria
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Experiment Specification
Experiment Specification | Instructions are provided as comments in the rows
ID
Reference to Test Specification
Title of Experiment
Research Infrastructure
Description
Diagram Reference
Experiment Realisation
Description
Diagram Reference
Experiment Setup
Description
Diagram Reference
Experimental Design and Justification
Description
Diagram Reference
Precision of equipment and measurement uncertainty
Storage of experiment data
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## 4
Test Case | Instructions are provided as comments in the rows
| ID | 4
| Name of the Test Case | Investigation of different voltage control techniques for inverter-interfaced DERs in microgrids
Version management
| Author | A. Paspatis, A. Kontou, A. F. Cortés Borray, Julia Merino
| Version | 3
| Project | ERIGRID 2.0
| Date | 13/04/2021
Narrative
| Description | A microgrid with inverter-interfaced distributed energy resources (DERs) is considered. In order to respect the system regulations and successfully feed the microgrid load, the voltage across the microgrid needs to be regulated close to its nominal value. Through the control design of the inverter-interfaced distributed energy resources, different control schemes are investigated. In particular i) master-slave voltage control, ii) conventional droop grid-forming control and iii) inverse droop grid-forming control.
Diagram reference
Function(s) under Investigation (FuI)
| Description | Voltage regulation in a microgrid with inverter-interfaced DERs
Diagram reference
Object under Investigation (OuI)
| Description | Inverter-interfaced distributed energy resources controllers
Diagram reference
Domain under Investigation (DuI)
| Description | Electrical Power Control systems
Diagram reference
Purpose of Investigation (PoI)
| Description | Comparison of different voltage control schemes
Diagram reference
System under Test (SuT)
| Description | A microgrid that hosts multiple inverter-interfaced distributed energy resources, lines, loads, etc.
Diagram reference
Functions under Test (FuT)
| Description | Different voltage control schemes to achieve microgrid load voltage regulation
Diagram reference
| Test criteria (TCR) | Microgrid operation according to the designed control algorithm
| Target Metrics (TM) | 1. Voltage measured at the output of the inverter (Is proper voltage regulation achieved?) 1. Number of interruptions (Is continuity of service achieved after a sudden change in the demand and/or output of RES, or a generator outage?) 1. Overall performance (What are the advantages and disadvantages of each technique?)
| Variability Attributes (VA) | 1. Different microgrid loading 1. Different line impedance nature (i.e., resistive or inductive or complex)
| Quality Attributes (QA) | Microgird voltages inside the ±5% of the nominal voltage / Successful
Qualification Strategy
| Description | The most common voltage control algorithms for inverter-based microgrids will be validated through three tests, one for each control technique, where the inverters forming the inverter-based microgrid will be equipped with the appropriate voltage control algorithm. Then, the results will be collected to perform the comparison between the different voltage control techniques.
Diagram reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## 4.01
Test Specification | Instructions are provided as comments in the rows
| ID | 4.01
| Reference to Test Case | TC4
| Title of Test | Performance of different voltage control techniques for inverter-interfaced DERs in microgrids
Test Rationale
| Description | This test will perform a comparison between different voltage control schemes that are widely used in inverter-based microgrids, i.e., master-slave control, conventional droop control and inverse droop control. Aiming to quantify the effectiveness of the aforementioned techniques, their pros & cons will be ultimately identified.
Diagram Reference
Specific Test System
| Description | Laboratory setup
| Diagram Reference | Lab_setup.png
| Target measures | Microgrid voltages
| Input and output parameters | Input: - Level of unbalance of the load - Inverter power injection set-points and limits - DERs control parameters - Microgrid characteristics Output: - Microgrid voltages
Test Design
| Description | 1. Operate multiple inverters in parallel 1. Perform load changes and observe voltage regulation (continuity of service) 1. Save the experimental results
Diagram Reference
| Initial system state | - Inverter controllers enabled - Load disconnected - Grid voltages based on the nominal output values of the inverters - Hardware or simulated network and devices up and running - Power analyzer and computers displaying and saving data
| Evolution of system state and test signals | The microgrid system is subjected to load variations (step changes)
| Other parameters | N/A
| Temporal resolution | At least 0.1 ms.
| Source of uncertainty | Impedance of load and lines, inverter sensors operation
| Suspension criteria / Stopping criteria | Abnormal current/ power injections from inverters or tripping of inverters
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
| Diagram id | image1.png
| Diagram name | image1.png
| Diagram URI type | image
| Diagram URI value | image1.png

## 4.01.01
Experiment Specification | Instructions are provided as comments in the rows
| ID | 4.01.01
| Reference to Test Specification | 4.01
| Title of Experiment | Master-slave voltage control
Research Infrastructure
| Description | Electric Energy Systems Laboratory (ICCS-NTUA)
Diagram Reference
Experiment Realisation
| Description | Multiple inverters forming a microgrid, both through hardware setup and through simulated components in the RTDS
Diagram Reference
Experiment Setup
| Description | 1. Hardware controller (e.g., Three-phase real-time computer) 1. Simulated microgrid network and inverters in the RTDS 1. Optional: Hardware inverter (e.g., Three-phase inverter)
Diagram Reference
Experimental Design and Justification
Description
Diagram Reference
| Precision of equipment and measurement uncertainty | Software and power analyzer are of high precision, inverter sensing system may be of lower precision
| Storage of experiment data | Power analyzer and computer memory
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## 4.01.02
Experiment Specification | Instructions are provided as comments in the rows
| ID | 4.01.02
| Reference to Test Specification | 4.01
| Title of Experiment | Conventional droop grid-forming control
Research Infrastructure
| Description | Electric Energy Systems Laboratory (ICCS-NTUA)
Diagram Reference
Experiment Realisation
| Description | Multiple inverters forming a microgrid, both through hardware setup and through simulated components in the RTDS
Diagram Reference
Experiment Setup
| Description | 1. Hardware controller (e.g., Three-phase real-time computer) 1. Simulated microgrid network and inverters in the RTDS 1. Optional: Hardware inverter (e.g., Three-phase inverter)
Diagram Reference
Experimental Design and Justification
Description
Diagram Reference
| Precision of equipment and measurement uncertainty | Software and power analyzer are of high precision, inverter sensing system may be of lower precision
| Storage of experiment data | Power analyzer and computer memory
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## 4.01.03
Experiment Specification | Instructions are provided as comments in the rows
| ID | 4.01.03
| Reference to Test Specification | 4.01
| Title of Experiment | Inverse droop grid-forming control
Research Infrastructure
| Description | Electric Energy Systems Laboratory (ICCS-NTUA)
Diagram Reference
Experiment Realisation
| Description | Multiple inverters forming a microgrid, both through hardware setup and through simulated components in the RTDS
Diagram Reference
Experiment Setup
| Description | 1. Hardware controller (e.g., Three-phase real-time computer) 1. Simulated microgrid network and inverters in the RTDS 1. Optional: Hardware inverter (e.g., Three-phase inverter)
Diagram Reference
Experimental Design and Justification
Description
Diagram Reference
| Precision of equipment and measurement uncertainty | Software and power analyzer are of high precision, inverter sensing system may be of lower precision
| Storage of experiment data | Power analyzer and computer memory
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value