## HTD Template Information
Version | V1.3
Mandatory: All the cells in Column C in yellow have to be completed mandatorily.
Optional: The cells in blue are for multiple objects, that can be completed when needed.

## Test Case
Test Case | Instructions are provided as comments in the rows
ID
Name of the Test Case
Version management
Author
Version
Project
Date
Narrative
Description
Diagram reference
Function(s) under Investigation (FuI)
Description
Diagram reference
Object under Investigation (OuI)
Description
Diagram reference
Domain under Investigation (DuI)
Description
Diagram reference
Purpose of Investigation (PoI)
Description
Diagram reference
System under Test (SuT)
Description
Diagram reference
Functions under Test (FuT)
Description
Diagram reference
Test criteria (TCR)
Target Metrics (TM)
Variability Attributes (VA)
Quality Attributes (QA)
Qualification Strategy
Description
Diagram reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Test Specification
Test Specification | Instructions are provided as comments in the rows
ID
Reference to Test Case
Title of Test
Test Rationale
Description
Diagram Reference
Specific Test System
Description
Diagram Reference
Target measures
Input and output parameters
Test Design
Description
Diagram Reference
Initial system state
Evolution of system state and test signals
Other parameters
Temporal resolution
Source of uncertainty
Suspension criteria / Stopping criteria
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Experiment Specification
Experiment Specification | Instructions are provided as comments in the rows
ID
Reference to Test Specification
Title of Experiment
Research Infrastructure
Description
Diagram Reference
Experiment Realisation
Description
Diagram Reference
Experiment Setup
Description
Diagram Reference
Experimental Design and Justification
Description
Diagram Reference
Precision of equipment and measurement uncertainty
Storage of experiment data
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## 6
Test Case | Instructions are provided as comments in the rows
| ID | 6
| Name of the Test Case | Evaluation of frequency restoration response in islanded power system
Version management
| Author | E. Rikos, L.Pellegrino, R. Lazzari
| Version | 1.1
| Project | ERIGrid 2.0-NA4
| Date | 01/12/2020
Narrative
| Description | One of the important functionalities of a microgrid is its ability to operate in islanded mode when the conditions of the system necessitate that. In such a mode the islanded microgrid should provide the functionalities to keep the frequency stable. With these functionalities the microgrid controllers (local and central) should contain frequency deviations and restore each deviation to zero from the nominal value. This test case examines the effectivity of the frequency restoration control of the microgrid under various operating conditions.
Diagram reference
Function(s) under Investigation (FuI)
| Description | - Secondary/tertiary frequency control
Diagram reference
Object under Investigation (OuI)
| Description | - Microgrid Frequency Controller (MFC)
Diagram reference
Domain under Investigation (DuI)
| Description | - Electrical - ICT (time-delays) - Electrochemical - Thermal - Environmental
Diagram reference
Purpose of Investigation (PoI)
| Description | - Validation of the controller/s for frequency stability and steady-state error elimination during restoration phase.
Diagram reference
System under Test (SuT)
| Description | The main components and subsystems that are of interest for this TC are depicted in the above diagram and summarized below: - Microgrid Frequency Controller (MFC) - Load Controllers - CHP microturbines - Battery inverters - RES inverters - Communication channels
| Diagram reference | TC06_SuT.png
Functions under Test (FuT)
| Description | - Battery Management System (BMS) - Maximum Power Point Tracker (MPPT) - Inverter control (Grid Forming, Grid Following, Grid Supporting) - CHP control (Heat or Power Priority) - Load control - Supervisory Control and Data Acquisition (SCADA) - Energy Management System (EMS) - Local droop control - Local inertia control
Diagram reference
| Test criteria (TCR) | - Frequency response
| Target Metrics (TM) | - Frequency Restoration time - Steady-state frequency deviation (after restoration) - Frequency oscillations damping factor (trumpet curve) - Remaining reserves (power/energy) - DERs curtailment - Loads curtailment
| Variability Attributes (VA) | Fully Controllable attributes: - Grid topology - Droop control parameters - Inverters control functionalities Partly Controllable attributes: - Loads active/reactive power - Generators active/reactive power Uncontrollable attributes: - Solar irradiation - Wind speed - Ambient temperature - ICT and control delays
| Quality Attributes (QA) | - Sampling time of signals (frequency and power flows): 100ms - Resolution: - frequency 0.05Hz, - power 0.01 pu - Points of measurement: - Frequency: at least 1 (at the point of common coupling) - Power: 1 point for each resource connected at their electrical output - Size of imbalance disturbance: >20% - Environmental conditions: - Enough solar irradiation and wind speed so that the combined RES portfolio produces at least 20% of its maximum power - State of Charge: between 35% and 90% - Load: at least 20%
Qualification Strategy
| Description | The selected PoI can be tackled by one Test Specification only in which only some input variables or system parameters need be changed over the test repetitions in order to achieve the desired results. In other words, aspects such as the main grid topology remain unchanged except for small reconfigurations. In our TC this topology is selected to be a LV distribution grid. Also, in order to validate the frequency response of the islanded microgrid, no specific tests are prerequisite to determine parameters and variable values necessary to conduct the main test.
Diagram reference
Diagrams
| Diagram id | TC06_SuT.png
| Diagram name | System under Test
| Diagram URI type | image
| Diagram URI value | TC06_SuT.png

## TC6.TS1
Test Specification | Instructions are provided as comments in the rows
| ID | TC6.TS1
| Reference to Test Case | TC6
| Title of Test | Validation of islanded microgrid ability to restore frequency deviations in a stable manner
Test Rationale
| Description | This test allows us to validate the ability of core components of the microgrid to effectively respond and tackle imbalances that result in frequency deviations. These core components include the MFC, the DER units that provide reserves as well as communication parts that can influence the stability of the control due to time delays.
Diagram Reference
Specific Test System
| Description | The above test system is based on the LV distribution network benchmark application example by CIGRE1
| Diagram Reference | TC06.01_STS.png
| Target measures | - Restoration time <120s - Steady-state deviation: <0.1Hz - Reserves’ availability: >20% - DERs curtailment: <30% - Loads curtailment: <5%
| Input and output parameters | Input parameters - Solar irradiance - Wind speed - Ambient temperature - Load consumption - Breaker state Output parameters - Frequency - State-of-Charge - Power of Reserves
Test Design
| Description | The test considers several consecutive imbalances and frequency deviations. This is needed to sufficiently evaluate the capability of the frequency control system to cope with these incidents. It is possible that the initial state of the microgrid grid-connected with the exchange of power with the utility grid. At the beginning of the test the circuit breaker can be opened to isolate the microgrid and cause a disturbance in the power balance.
Diagram Reference
| Initial system state | - The circuit breaker at the PCC is open. Alternatively, it can be opened right after the start of the test as a potential disturbance source. - The combination of the RES units should provide at least 20% of their nominal power. - The consumption of the loads should be at least 20% of the maximum consumption. - The battery SOC should be between 40 and 60% - The imbalance should be under 5%.
| Evolution of system state and test signals | - The microgrid starts in islanded mode or in grid-connected mode. - Firstly, the system is sufficiently balanced so that a small number of reserves (ideally zero) are implemented and the frequency is nominal (50Hz). - One imbalance emerges which leads to significant frequency deviation and the consequent activation of a large part of reserves. - Subsequent disturbances emerge either before or after the restoration of frequency to its nominal value.
| Other parameters | N/A
| Temporal resolution | Monitoring quantities should have a maximum sampling time of 0.1s.
| Source of uncertainty | Environmental conditions Consumers’ demand Grid parameters variability i.e., resistance/inductance ratio
| Suspension criteria / Stopping criteria | The test should be suspended and restarted if one of the quality attributes described in the TC is not met. Also, suspension may be due to deviation from the desired initial conditions described above.
Mapping to Research Infrastructure
| Description | Our final goal of the mapping step is to produce as many as possible among a number of different testing approaches. These approaches include: pure simulation of the system either as a monolithic or as a co-simulation approach. Real-time simulation, primarily in the form of CHIL (PHIL is also possible). Purely physical implementation where a mock-up of the benchmark grid is used in laboratory environment.
Diagram Reference
Diagrams
| Diagram id | image2.png
| Diagram name | image2.png
| Diagram URI type | image
| Diagram URI value | image2.png