## HTD Template Information
Version | V1.3
Mandatory: All the cells in Column C in yellow have to be completed mandatorily.
Optional: The cells in blue are for multiple objects, that can be completed when needed.

## Test Case
Test Case | Instructions are provided as comments in the rows
ID
Name of the Test Case
Version management
Author
Version
Project
Date
Narrative
Description
Diagram reference
Function(s) under Investigation (FuI)
Description
Diagram reference
Object under Investigation (OuI)
Description
Diagram reference
Domain under Investigation (DuI)
Description
Diagram reference
Purpose of Investigation (PoI)
Description
Diagram reference
System under Test (SuT)
Description
Diagram reference
Functions under Test (FuT)
Description
Diagram reference
Test criteria (TCR)
Target Metrics (TM)
Variability Attributes (VA)
Quality Attributes (QA)
Qualification Strategy
Description
Diagram reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Test Specification
Test Specification | Instructions are provided as comments in the rows
ID
Reference to Test Case
Title of Test
Test Rationale
Description
Diagram Reference
Specific Test System
Description
Diagram Reference
Target measures
Input and output parameters
Test Design
Description
Diagram Reference
Initial system state
Evolution of system state and test signals
Other parameters
Temporal resolution
Source of uncertainty
Suspension criteria / Stopping criteria
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Experiment Specification
Experiment Specification | Instructions are provided as comments in the rows
ID
Reference to Test Specification
Title of Experiment
Research Infrastructure
Description
Diagram Reference
Experiment Realisation
Description
Diagram Reference
Experiment Setup
Description
Diagram Reference
Experimental Design and Justification
Description
Diagram Reference
Precision of equipment and measurement uncertainty
Storage of experiment data
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## 16
Test Case | Instructions are provided as comments in the rows
| ID | 16
| Name of the Test Case | Testing Black-Start capability using distributed converted interfaced resources
Version management
| Author | Evangelos Rikos, Julia Merino, Andres Cortes
| Version | 1.0
| Project | ERIGrid 2.0-NA4
| Date | 22/02/2021
Narrative
| Description | The focus of this TC is on MV distribution grid where one central controller can perform the following actions: isolate/disconnect/ reconnect lines and/or resources and initiate grid-forming DGs. The DGs that provide the BS service should have resilience in significant frequency/voltage variations to cope with large imbalances during re-energization and for a typical duration of at least 1 hour. The scope of the TC is to verify the system’s ability to achieve a smooth re-energization within the prescribed duration.
Diagram reference
Function(s) under Investigation (FuI)
| Description | - Black-start control - Primary voltage control - Primary frequency control - Secondary frequency control - Secondary voltage control
Diagram reference
Object under Investigation (OuI)
| Description | - Distribution Management System (as the provider of the BS and secondary control functionalities) - Inverter-based DGs (as providers of the power/energy needed for system re-energization and as primary control resources)
Diagram reference
Domain under Investigation (DuI)
| Description | - Electrical Power - ICT (time-delays) - Electrochemical - Environmental
Diagram reference
Purpose of Investigation (PoI)
| Description | - Validation of Black-Start capability
Diagram reference
System under Test (SuT)
| Description | The main components and subsystems that are of interest for this TC are depicted in the above diagram and summarized below: - Distribution Management System (DMS) - Circuit breakers - Battery energy storage system (BESS) - Distribution Grid
| Diagram reference | TC16_SuT.png
Functions under Test (FuT)
| Description | - Battery Management System - MPPT - Load control - SCADA - Energy Management System
Diagram reference
| Test criteria (TCR) | - Frequency response - Voltage response - Battery capacity
| Target Metrics (TM) | - Maximum Voltage deviations (±5%) - Maximum frequency deviations (47.5 Hz–52 Hz) - Maximum ROCOF - Response/stabilization time - Maximum Energy Availability - Number of sequential start-ups (at least three)
| Variability Attributes (VA) | Fully Controllable attributes: - Circuit breakers’ state - Primary and secondary control parameters - Inverter control functionalities Partly Controllable attributes: - Loads’ active/reactive power - Generators’ active/reactive power Uncontrollable attributes: - Solar irradiation - Wind speed - Ambient temperature - ICT and control delays
| Quality Attributes (QA) | - Sampling time of signals (frequency, voltages, Power/energy flows): <1sec - Resolution: - frequency 0.05 Hz, - voltage 0.005 pu - Power 0.01pu - Points of measurement: - Frequency: at least 1 - Voltage: 1 point for each resource connected at their electrical output - Battery power/energy flow: 1 point at the output of the BESS
Qualification Strategy
| Description | In order to meet the specific PoI, which is the evaluation of the distribution system’s Black Start capability, three separate test specifications are required: -One test is related to the partitioning of the system. That is how the centralized BS controller manages to disconnect and reconnect components of the grid, either resources (loads, generators) or lines. The test validates the correctness of the disconnection order of components, as well as the ability of the controller to reconnect them at times when voltage and frequency are well within specific boundaries and more or less stable. -The second test verifies the ability of the system to maintain voltage and frequency within specific boundaries after the BS generator is started up by the BS central controller. The specific operating limits for this test are more relaxed as opposed to the ones that apply in normal operation. -The third test is a sort of endurance test which validates the BS generator’s ability to provide the service for a minimum time duration (e.g., 1 hour). In other words, this test comes down to verifying the energy reserve of the BS generator.
Diagram reference
Diagrams
| Diagram id | TC16_SuT.png
| Diagram name | System under Test
| Diagram URI type | image
| Diagram URI value | TC16_SuT.png

## 16.01
Test Specification | Instructions are provided as comments in the rows
| ID | 16.01
| Reference to Test Case | TC16
| Title of Test | Black Start algorithm verification
Test Rationale
| Description | This test verifies the ability of the centralized BS controller to disconnect/reconnect parts of the grid and resources in the right order and at the right timing. The order of actions is fixed and predefined through the programming parameters of the control system, whereas the reconnection timing should happen automatically at times when voltage and frequency are within specific boundaries.
Diagram Reference
Specific Test System
| Description | The test setup depicted above comprises one BS controller (as part of the DMS), three loads with controllable switches, three transducers for the voltage measurement at each load (on the breaker’s side), one transducer for the measurement of frequency and one controllable source which provides the voltage/frequency controllability required for validating the controller behavior.
| Diagram Reference | TC16.01_STS.png
| Target measures | - Power outage time - Reconnection times - Voltage/frequency values
| Input and output parameters | Input parameters - Frequency - Voltage Output parameters - Breaker state - Load voltage - Controllable source activation
Test Design
| Description | The specific test makes use of the controllable MV source to emulate the blackout condition as well as the BS generation provider. Therefore, the source’s output can be deactivated manually and reactivated through a communication signal from the BS controller. In the real system, the specific signal is the start-up command from the BS controller to the BS generator. The voltages at each load should be monitored on either end of the breaker in order to verify: - Disconnection/reconnection time - If the voltage conditions for reconnection are suitable Moreover, by monitoring the frequency at the source’s output it is possible to: - Verify that the controller reconnects the loads within the proper frequency conditions and in the right order - Verify that the start-up command to the BS generator is communicated correctly and in the right order Even though some voltage/frequency stability is presumed for the test, the limits for these values, especially frequency should be not considered as tight as in normal operation. Therefore, the frequency limits for this test are considered from 47.5 to 52 Hz with a ROCOF <2 Hz/s. The corresponding voltage limits are considered as +5% and -5% of the nominal voltage.
Diagram Reference
| Initial system state | - The controllable source supplies the system with constant voltage at frequency at nominal values (fsource=50 Hz, Vsource=1 p.u.) - The three breakers are closed, and the loads are supplied - The BS controller is reset to its initial state (normal operation) - The BS controller continuously monitors frequency and voltages in order to detect a possible blackout
| Evolution of system state and test signals | - At a predetermined moment, the source’s output is deactivated and the voltage and frequency become zero emulating the blackout conditions - This time is recorded as reference for calculating the response times of the various components - The BS controller detects the loss of voltage and initiates the BS procedure - Initially, the BS controller disconnects all three loads from the grid - After a specific interval (<1 min), the BS controller dispatches the start-up signal to the controllable source - The output of the source is monitored in order to calculate the time required for this step until re-energization is restored - The BS controller continuously monitors the voltages and frequency in order to detect when the conditions are proper for reconnecting the loads - The load voltages are recorded to measure the reconnection order as well as the proper voltage/frequency conditions during reconnection
| Other parameters | N/A
| Temporal resolution | A sampling time of <1 s is enough for this test to provide the necessary information since the responses of the controller signals range in the order of several seconds to minutes.
| Source of uncertainty | Uncertainties that may appear in this test are due to the precision of the various instruments used to measure the voltage/frequency responses. Additional uncertainties may be introduced by the communication channel delays between the BS controller and the various controllable components.
| Suspension criteria / Stopping criteria | The test should be suspended and restarted if one of the quality attributes described in the TC is not met or if the algorithmic procedure of the BS controller does not perform as should be expected.
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
| Diagram id | image2.png
| Diagram name | image2.png
| Diagram URI type | image
| Diagram URI value | image2.png

## 16.02
Test Specification | Instructions are provided as comments in the rows
| ID | 16.02
| Reference to Test Case | TC16
| Title of Test | Frequency and Voltage stability response during BS
Test Rationale
| Description | Once the BS generator is started by the BS controller to reenergize the grid, an interval follows within which several resources are reconnected. The main challenge that the BS generator and the system itself faces is the stability of frequency and voltage. Due to its nature, the requirements for this operating state should not be very strict. Nevertheless, rudimentary stability should always be maintained in order to avoid a new blackout. This test aims at evaluating the system’s capability to cope with the imbalances and maintain frequency as well as voltage stability within the required limits.
Diagram Reference
Specific Test System
| Description | The above test system is based on the MV distribution network benchmark application example by CIGRE1
| Diagram Reference | TC16.02_STS.png
| Target measures | - ΔVmax=+5% to -5% of nominal voltage - Δfmax= from 47.5 to 52 Hz with a ROCOF <2 Hz/s.
| Input and output parameters | Input parameters - Solar irradiance - Wind speed - Ambient temperature - Load consumption - Breaker state Output parameters - Frequency - Voltages
Test Design
| Description | The test is carried out in a way that emulates the system behaviour after a black out. This implies the initial disconnection of lines and loads through the controllable circuit breakers and the start-up of the BS generator (BESS on Bus B-5). In this way, the system is sectionalized to its minimal connectivity state.
Diagram Reference
| Initial system state | - All circuit breakers are open - The BS generator is not running
| Evolution of system state and test signals | - At a specific time within 1 min from the beginning of the test, the BS generator is started up - Frequency and voltages at various points of the grid are continuously monitored - After another time interval (e.g., 2-5 minutes) the first set of circuit breakers is reclosed to add the extra generation/load to the system. The time interval allowed for reconnection should be enough for quasi-stabilization of the system. - The previous step is repeated as many times as the number of circuit breaker groups are reclosed
| Other parameters | N/A
| Temporal resolution | A sampling time of <100 ms is required for the accurate measurement of frequency and voltage variations.
| Source of uncertainty | Apart from the measurement uncertainties due to the instruments’ accuracy, additional uncertainties may be introduced by the communication channel delays between the controller and the DER units. In addition to that, the system operation is subject to uncertainties due to: Environmental conditions Consumers’ demand Grid parameters variability, i.e., resistance and inductance
| Suspension criteria / Stopping criteria | The test should be suspended and restarted if one of the quality attributes described in the TC is not met. If stability is not ensured during the various reconnection actions, the control parameters should be readjusted and the test repeated.
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
| Diagram id | image3.png
| Diagram name | image3.png
| Diagram URI type | image
| Diagram URI value | image3.png

## 16.03
Test Specification | Instructions are provided as comments in the rows
| ID | 16.03
| Reference to Test Case | TC16
| Title of Test | BS generator energy availability test
Test Rationale
| Description | The BS generator must provide a sufficient amount of energy for at least 1 hour, in order for the system to cope with any uncertainties during the process. Such uncertainties may include failures in starting up other generators or instability problems. Also, uncertainties caused State of Health (SOH), ambient temperature, etc. may result in a deviation of the actual available energy of the BESS from its nominal value. The specific test addresses the ability of the BS generator to provide energy supply for at least 1 hour of continuous operation after the BS.
Diagram Reference
Specific Test System
| Description | The test system consists of a controllable and bidirectional MV source, one BESS comprising battery, inverter and BMS and one controller which can control the BESS’s active and reactive power injection.
| Diagram Reference | TC16.03_STS.png
| Target measures | - Battery SOC>10% - Operation time >1 h
| Input and output parameters | Input parameters - Ambient temperature - Active and reactive power setpoints Output parameters - Active and Reactive Power - Active and Reactive Energy - SOC
Test Design
| Description | The test can consider various profiles for the setpoints of P and Q depending on the specifications and needs from each BS system. However, as the worst-case scenario, the maximum P should continuously be drawn from the BESS in order to examine the minimum time duration of the generator’s availability.
Diagram Reference
| Initial system state | - The battery is charged at a SOC>50% assuming that the system may participate in other services as well - The MV source is up and running at nominal voltage - The Inverter is connected to the MV source
| Evolution of system state and test signals | - The PQ controller changes the setpoint for the active power to its maximum value. - The power flow is recorded at the bus together with the time that the flow of energy starts - In parallel, the SOC and battery voltage are monitored through the BMS - The discharging of the BESS continues until either 1-hour elapses or the SoC drops below 10%
| Other parameters | N/A
| Temporal resolution | A sampling time of 1 s is sufficient for monitoring the required quantities
| Source of uncertainty | Sources of uncertainty for this experiment may be the SoH of the battery, the ambient temperature as well as the accuracy with which the BMS calculates the SOC. In addition, accuracies of measurement equipment may apply.
| Suspension criteria / Stopping criteria | The test should be suspended if no maximum power absorption is obtained from the BESS. Also, if for some reason the BMS overrides the external control in order to prioritize other functions (e.g., recharge of the battery).
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
| Diagram id | image4.png
| Diagram name | image4.png
| Diagram URI type | image
| Diagram URI value | image4.png