## HTD Template Information
Version | V1.3
Mandatory: All the cells in Column C in yellow have to be completed mandatorily.
Optional: The cells in blue are for multiple objects, that can be completed when needed.

## Test Case
Test Case | Instructions are provided as comments in the rows
ID
Name of the Test Case
Version management
Author
Version
Project
Date
Narrative
Description
Diagram reference
Function(s) under Investigation (FuI)
Description
Diagram reference
Object under Investigation (OuI)
Description
Diagram reference
Domain under Investigation (DuI)
Description
Diagram reference
Purpose of Investigation (PoI)
Description
Diagram reference
System under Test (SuT)
Description
Diagram reference
Functions under Test (FuT)
Description
Diagram reference
Test criteria (TCR)
Target Metrics (TM)
Variability Attributes (VA)
Quality Attributes (QA)
Qualification Strategy
Description
Diagram reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Test Specification
Test Specification | Instructions are provided as comments in the rows
ID
Reference to Test Case
Title of Test
Test Rationale
Description
Diagram Reference
Specific Test System
Description
Diagram Reference
Target measures
Input and output parameters
Test Design
Description
Diagram Reference
Initial system state
Evolution of system state and test signals
Other parameters
Temporal resolution
Source of uncertainty
Suspension criteria / Stopping criteria
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Experiment Specification
Experiment Specification | Instructions are provided as comments in the rows
ID
Reference to Test Specification
Title of Experiment
Research Infrastructure
Description
Diagram Reference
Experiment Realisation
Description
Diagram Reference
Experiment Setup
Description
Diagram Reference
Experimental Design and Justification
Description
Diagram Reference
Precision of equipment and measurement uncertainty
Storage of experiment data
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## TC1
Test Case | Instructions are provided as comments in the rows
ID
| Name of the Test Case | Fault tolerance/ recovery of a multi-aggregator dispatch mechanism
Version management
Author
Version
| Project | ERIGrid 2.0
| Date | 5/2/2021
Narrative
| Description | In a section of an electrical distribution grid, multiple (>=2) aggregators operate independently of each other. Each of the aggregators maintains a portfolio of flexible DER units under contract. The contract provides for on-demand delivery of a grid service (e.g. load reduction/production increase). It is assumed that the primary customer for the grid service in question is the local DSO operating the grid section. It is also assumed that a fair mechanism exists for matching supply (aggregators) and demand (DSO). This mechanism could e.g. be a flexibility market - but the exact workings are not relevant to the test case. For the sake of simplicity, it is assumed that the unknown mechanism has produced a merit-order list of the services offered by the different aggregators, before the start of the test. A dispatch unit is tasked with continuously matching the service demand indicated by the DSO using the merit order list, and to submit service activation requests to the appropriate aggregators. At some point in time after the start of the test, a communication fault disrupts communication between the dispatch unit and one of the aggregators. To ensure that the service demand is met, the dispatch unit must decide whether the fault is temporary or permanent, and arrange for meeting the service demand with the remaining aggregator(s). It is assumed that an aggregator affected by a communication fault will continue to function, i.e. service definitions agreed with the dispatch unit will continue to be delivered. However, due to the lack of updates from the dispatch unit, these services will eventually diverge from the evolving needs of the grid.
Diagram reference
Function(s) under Investigation (FuI)
| Description | Communication fault detection and impact mitigation. A communication fault in the context of this test case is defined as the inability of the dispatch unit to communicate with one or more aggregators, caused by a disruption of the communication link. Implementations of the two functions will typically require functionality both on the dispatch unit as well as on the aggregator side.
Diagram reference
Object under Investigation (OuI)
| Description | Aggregator dispatch unit
Diagram reference
Domain under Investigation (DuI)
| Description | - Electrical - ICT
Diagram reference
Purpose of Investigation (PoI)
| Description | Characterisation of (the performance of) system recovery from a permanent communication failure.
Diagram reference
System under Test (SuT)
| Description | The test system consists of an electrical grid section, energy resources, aggregators, a dispatch unit, a service requester (DSO) and an ICT command and control infrastructure. The electrical grid section is a part of a LV and/or MV distribution grid (e.g. 0.4kV and 10kV) with a number of flexible DER units distributed across one or multiple feeders. The ICT infrastructure consists of three separate types of IT systems (dispatch unit, aggregator and DER controller) as well as the communication links between these entities.
Diagram reference
Functions under Test (FuT)
| Description | - Communication fault detection and impact mitigation (FuI) - Coordinated congestion management, consisting of an algorithm for congestion management as well as the communication between units needed to implement the algorithm (i.e. between unit controllers and aggregators and between aggregators and dispatch unit) - Aggregator internal dispatch mechanism, consisting of portfolio management and unit dispatch - Unit controller functionality, consisting of local flexibility calculation and management - A dispatch mechanism for aggregators, executing on the dispatch unit. - A congestion detection method, emulating the determination of service requirements by a DSO.
Diagram reference
| Test criteria (TCR) | - Time to detection of a nonresponsive aggregator - Time to full service restoration
| Target Metrics (TM) | - Time elapsed from the occurrence of a communication fault to the classification of an aggregator as nonresponsive by the dispatch unit [s] - Time elapsed from the occurrence of a communication fault to the restoration of a stable steady state in which the entire service demand as requested by the DSO is met by the aggregators [s].
| Variability Attributes (VA) | - Controllable - Frequency of service change requests from dispatch unit to aggregators [1/10s to 1/10min] - Duration of communication failure [100ms to permanent] - Variability of baseload profile [0 to 100% of mean baseload]
| Quality Attributes (QA) | - Confidence in the accuracy of the time measurements (measurement error <= +/- 10% of measured value)
Qualification Strategy
| Description | The system will be characterized in two different domains: - Isolated in the ICT domain: How well does the multi-aggregator system recover from a communication fault? - The overall performance of the system in the electrical power domain: What is the impact of the fault recovery in the ICT domain on the ability of the multi-aggregator system to deliver a power system service? This will be achieved by a sequence of two tests: - One test to determine the performance of a multi-aggregator system without any communication fault recovery mechanism. This will establish a baseline for overall system performance in the electrical power system domain. - A second test where a recovery mechanism is in place. This will allow both characterization objectives to be achieved by (a) measuring the performance of the fault recovery mechanism in the ICT domain, and (b) comparing the performance of the entire multi-aggregator system to the baseline results.
Diagram reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## TC17.TS1
Test Specification | Instructions are provided as comments in the rows
| ID | TC17.TS1
| Reference to Test Case | TC17
| Title of Test | Baseline test
Test Rationale
| Description | This test will establish the performance of the dispatch mechanism in the absence of a fault recovery mechanism by establishing the (permanent) performance loss of the dispatcher as a result of a permanent loss of one aggregator from its portfolio. This performance loss will express itself in a degradation of the dispatcher’s ability to track a setpoint, and will depend on the amount of flexibility which can be taken over by the remaining aggregator(s).
Diagram Reference
Specific Test System
Description
| Diagram Reference | image1.png
| Target measures | Deviation of service delivered from service requested
| Input and output parameters | - Input: Level of base load [kW] - Input: Service requested (by DSO) to dispatch unit - Input: Time of fault occurrence [s] - Output: Active power production/consumption at individual DERs [kW] - Output: Active power sum flow at grid connection [kW]
Test Design
| Description | The test can be performed as a hardware experiment, a simulation experiment or a combination of the two. - Configure grid, DER units and base load to bring system into initial state (t=t0) - At t=t1, request a load relief service from the dispatch unit, wait for aggregators to activate DER units. Measure the effectiveness of the service delivery (impact on grid) after stabilization. - At t=t2, command fault simulator to disrupt communication to aggregator 1 - Continue measuring the effectiveness of the service delivery for a period to determine the magnitude of the mismatch between service requested and service delivered.
Diagram Reference
| Initial system state | - No service requested by dispatch unit - All DERs in neutral state (not delivering a service) - Feeder in overload condition by combined baseload+DER consumption - Fault simulator in bypass state (no fault)
| Evolution of system state and test signals | - Base load continues to change, following e.g. a random pattern - Aggregator response tracks changes in base load
Other parameters
| Temporal resolution | Electrical system measurements: 1s. Logging of ICT events (messages exchanged, communication fault event etc.) using timestamps with at least 1ms resolution.
| Source of uncertainty | Residual time synchronization difference between ICT entities
| Suspension criteria / Stopping criteria | Elapsed time (fixed length experiment)
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
| Diagram id | image1.png
| Diagram name | image1.png
| Diagram URI type | image
| Diagram URI value | image1.png

## TC17.TS2
Test Specification | Instructions are provided as comments in the rows
| ID | TC17.TS2
| Reference to Test Case | TC17
| Title of Test | Characterization of recovery from failure
Test Rationale
| Description | This test will characterize the response of the fault recovery mechanism. The results obtained will also allow a performance comparison with the baseline system.
Diagram Reference
Specific Test System
Description
| Diagram Reference | image1.png
| Target measures | - Time to restoration of service delivery - Deviation of service delivered from service requested
| Input and output parameters | - Input: Level of base load [kW] - Input: Service requested (by DSO) to dispatch unit - Input: Time of fault occurrence [s] - Output: Active power production/consumption at individual DERs [kW] - Output: Active power sum flow at grid connection [kW]
Test Design
| Description | The test can be performed as a hardware experiment, a simulation experiment or a combination of the two. - Configure grid, DER units and base load to bring system into initial state (t=t0) - At t=t1, request a load relief service from the dispatch unit, wait for aggregators to activate DER units. Measure the effectiveness of the service delivery (impact on grid) after stabilization. - At t=t2, command fault simulator to disrupt communication to aggregator 1 - Determine the points in time t=t3 where the dispatch unit has noticed the fault, and t=t4 where aggregator 2 has rescheduled. - Continuously measure the effectiveness of the service delivery in order to determine the disruption to service delivery during t3<t<t4. - Verify that the effectiveness of service delivery after t4 is comparable to before the fault (t<t2).
Diagram Reference
| Initial system state | - No service requested by dispatch unit - All DERs in neutral state (not delivering a service) - Feeder in overload condition by combined baseload+DER consumption - Fault simulator in bypass state (no fault)
| Evolution of system state and test signals | - Base load continues to change, following e.g. a random pattern - Aggregator response tracks changes in base load - Dispatch unit moves from “service delivery” to “fault recovery” and back to “service delivery”
Other parameters
| Temporal resolution | Electrical system measurements: 1s. Logging of ICT events (messages exchanged, communication fault event etc.) using timestamps with at least 1ms resolution.
| Source of uncertainty | Residual time synchronization difference between ICT entities
| Suspension criteria / Stopping criteria | Elapsed time (fixed length experiment)
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
| Diagram id | image1.png
| Diagram name | image1.png
| Diagram URI type | image
| Diagram URI value | image1.png