## HTD Template Information
Version | V1.3
Mandatory: All the cells in Column C in yellow have to be completed mandatorily.
Optional: The cells in blue are for multiple objects, that can be completed when needed.

## Test Case
Test Case | Instructions are provided as comments in the rows
ID
Name of the Test Case
Version management
Author
Version
Project
Date
Narrative
Description
Diagram reference
Function(s) under Investigation (FuI)
Description
Diagram reference
Object under Investigation (OuI)
Description
Diagram reference
Domain under Investigation (DuI)
Description
Diagram reference
Purpose of Investigation (PoI)
Description
Diagram reference
System under Test (SuT)
Description
Diagram reference
Functions under Test (FuT)
Description
Diagram reference
Test criteria (TCR)
Target Metrics (TM)
Variability Attributes (VA)
Quality Attributes (QA)
Qualification Strategy
Description
Diagram reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Test Specification
Test Specification | Instructions are provided as comments in the rows
ID
Reference to Test Case
Title of Test
Test Rationale
Description
Diagram Reference
Specific Test System
Description
Diagram Reference
Target measures
Input and output parameters
Test Design
Description
Diagram Reference
Initial system state
Evolution of system state and test signals
Other parameters
Temporal resolution
Source of uncertainty
Suspension criteria / Stopping criteria
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Experiment Specification
Experiment Specification | Instructions are provided as comments in the rows
ID
Reference to Test Specification
Title of Experiment
Research Infrastructure
Description
Diagram Reference
Experiment Realisation
Description
Diagram Reference
Experiment Setup
Description
Diagram Reference
Experimental Design and Justification
Description
Diagram Reference
Precision of equipment and measurement uncertainty
Storage of experiment data
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## 22
Test Case | Instructions are provided as comments in the rows
| ID | 22
| Name of the Test Case | Resilience Assessment of ICT infrastructure
Version management
Author
Version
| Project | ERIGrid 2.0
| Date | 28/04/21
Narrative
| Description | The broad aim of this test case is to quantify and assess the resilience of ICT equipment used for communication in Cyber Physical Systems (CPS), i.e., smart grids. More specifically, the focus is on cyber resilience of digital substations. In a digital substation, analogue signal wiring is replaced with digital Ethernet (IEEE 802.3) links. Communication within a digital substation is realized through the IEC 61850 standard that covers substation automation and protection functionalities. Communication with the control center is realized through a dedicated communication gateway using protocols such as IEC 60870-5-104 and/or DNP 3. CPS resilience assessment considers the impact on power grid operation, when the abovementioned protocols/standards in digital substations are subjected to disturbances or targeted cyber attacks – packet loss, denial of service, etc. The characterization of this performance is one of the major interests of this test case, considering the nature of communication effects, and their overall impact on grid operations.
Diagram reference
Function(s) under Investigation (FuI)
| Description | - Protection and automation functionality in a digital substation. - Type of data exchanged, i.e., control commands and measurements.
Diagram reference
Object under Investigation (OuI)
| Description | Digital substation (see SuT for more information)
Diagram reference
Domain under Investigation (DuI)
| Description | - Information and Communication Technology (ICT) - Electrical
Diagram reference
Purpose of Investigation (PoI)
| Description | Verification and characterization of cyber resilience of digital substations. Specifically, characterize and verify the impact of ICT infrastructure performance on grid operations, in a digital substation in the presence of: 1. Component failures in the ICT infrastructure of the substation 1. Misconfiguration of the ICT infrastructure 1. Cyber attacks targeting the substation ICT infrastructure The impact on grid operations is measured by noting how aforementioned factors affect protection functionality, i.e., tripping times in a digital substation.
Diagram reference
System under Test (SuT)
| Description | A digital substation includes substation bays, merging units, Ethernet switches (representing the process bus), Human Machine Interfaces (HMIs), time servers, Intelligent Electronic Devices (IEDs), Remote Terminal Units (RTUs), centralized protection and control units, station control systems, etc. A substation bay comprises busbars, disconnectors, circuit breakers, current and voltage transformers (CTs and VTs), etc. Hence, to realize this test case, the following components are required: - Real-time grid simulator such as RTDS or OPAL-RT that supports Hardware-in-Loop (HIL) studies - Substation network elements: 1. At least one ethernet switch and time server. At least two or more physical IEC 61850 capable IEDs 1. RTUs, MUs, other HIL devices - A communication network emulator/simulator to model disturbances/cyber attacks The testing involves interfacing the real-time grid simulator with all hardware components in a HIL setup to mimic a digital substation. Furthermore, the real-time grid simulator also needs to be interfaced with the network emulator to model and input communication related effects such as latency, packet loss, loss of service, etc. Source: Centralized Protection and Control.
| Diagram reference | image1.png
Functions under Test (FuT)
| Description | - Capability of the real-time grid simulator to exchange data using IEC 61850 and IEC 60870-5-104 - Automation and protection functionality realized by OuI - Behaviour and performance of IEDs within the SuT, when subjected to specific disturbances - Emulation of communication networks - Performance of communication network emulator, i.e., Mininet
Diagram reference
| Test criteria (TCR) | - Equipment response and performance under normal operating conditions - Equipment response and performance when subjected to communication-based disturbances – packet losses, latency, etc. - System response to communication-based disturbances
| Target Metrics (TM) | 1. Tripping times - During normal operating conditions - During disturbances 1. Communication of control commands (GOOSE) - During faulted (short-circuit) conditions - During communication disturbances
| Variability Attributes (VA) | - Type of protection scheme implemented - Overall substation configuration and topology - Characteristics of network emulator - Redundancy (N-1, N-2…. N-k): Number of components or communication links which can fail before system operation is at risk - Topology and type of simulated power system (transmission vs distribution) - Type of cyber-attack, e.g., Denial-of-Service (DoS), malformed authentication codes, etc.
| Quality Attributes (QA) | - Real-time communication performance during normal, electrical fault and communication disturbance conditions - Pass: performance within max threshold of 10 ms - Fail: performance exceeds 10 ms under any conditions
Qualification Strategy
| Description | The PoI are mainly addressed by characterizing and verifying the impact of ICT infrastructure performance on grid operations, in a digital substation. This can be achieved by determining how protection functionality and thereby power system stability is affected by disturbances to ICT infrastructure. - As per the IEC 61850 standard, the maximum tripping time for protection equipment should always be lesser than 10ms. Hence, this can be used as a metric to assess the cyber resilience of a digital substation. This assessment is subject to presence of component failures in the ICT infrastructure of the substation, misconfigurations, and cyber attacks targeting the substation ICT infrastructure.
Diagram reference
Diagrams
| Diagram id | image1.png
| Diagram name | image1.png
| Diagram URI type | image
| Diagram URI value | image1.png

## TC22.TS1
Test Specification | Instructions are provided as comments in the rows
| ID | TC22.TS1
| Reference to Test Case | TC22
| Title of Test | Determination of maximum tripping times in the presence of ICT disturbances within a digital substation
Test Rationale
| Description | The IEC 61850 standard recommends a maximum time for transmission of fast messages such as trip signals to be within 10ms. Hence, this experiment seeks to test this performance requirement under adverse communication related conditions such as packet losses, latency, etc.
Diagram Reference
Specific Test System
| Description | The test system comprises of a real-time grid simulator, at least one Ethernet switch, and multiple IEC 61850 devices interconnected in a HIL setup. See SuT for further information.
| Diagram Reference | image2.png
| Target measures | The maximum time taken to communicate trip signals when subjected to specific communication disturbances.
| Input and output parameters | Input parameters: - Type of power system simulated - Network topology of substation - Protection schemes applied through the relays - Fault type and duration - Type of disturbance: equipment failure, increased latency, bad actor, misconfiguration etc. Output parameters: - Maximum time taken to communicate trip signals
Test Design
| Description | The test is a HIL experiment as described in the SuT and specific test system. The test design is as follows: 1. Start the system with all devices functioning as required. 1. Run a test simulation with a short-circuit condition 1. Note that appropriate relay communicates trip signal via IEC 61850 GOOSE message 1. Circuit breaker is opened, and the fault is cleared 1. Note this tripping time as T1 1. Apply a specific type of communication disturbance, for e.g., increased network traffic via an external device or network emulator. 1. Repeat steps 2 to 4 and note the new tripping time T2. 1. Repeat steps 6 and 7 in case of equipment failures, misconfigurations, and note times as T3, T4, and so on.
Diagram Reference
| Initial system state | - All devices are ON and running - Real-time grid simulator can send and receive messages to and from the hardware devices
| Evolution of system state and test signals | Successful recording of parameters T1, T2…Tn for various types of ICT disturbances
| Other parameters | N/A
| Temporal resolution | Tens of milliseconds
| Source of uncertainty | Configuration of ethernet switch, IEC 61850 device compatibility
| Suspension criteria / Stopping criteria | Suspension criteria: Errors in devices/misconfiguration Stopping criteria: the experiment can be concluded when the maximum tripping times for various combinations of ICT disturbances and fault types are noted. Alternatively, if this time ever exceeds 10ms, the experiment can be stopped.
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
| Diagram id | image2.png
| Diagram name | image2.png
| Diagram URI type | image
| Diagram URI value | image2.png