## HTD Template Information
Version | V1.3
Mandatory: All the cells in Column C in yellow have to be completed mandatorily.
Optional: The cells in blue are for multiple objects, that can be completed when needed.

## Test Case
Test Case | Instructions are provided as comments in the rows
ID
Name of the Test Case
Version management
Author
Version
Project
Date
Narrative
Description
Diagram reference
Function(s) under Investigation (FuI)
Description
Diagram reference
Object under Investigation (OuI)
Description
Diagram reference
Domain under Investigation (DuI)
Description
Diagram reference
Purpose of Investigation (PoI)
Description
Diagram reference
System under Test (SuT)
Description
Diagram reference
Functions under Test (FuT)
Description
Diagram reference
Test criteria (TCR)
Target Metrics (TM)
Variability Attributes (VA)
Quality Attributes (QA)
Qualification Strategy
Description
Diagram reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Test Specification
Test Specification | Instructions are provided as comments in the rows
ID
Reference to Test Case
Title of Test
Test Rationale
Description
Diagram Reference
Specific Test System
Description
Diagram Reference
Target measures
Input and output parameters
Test Design
Description
Diagram Reference
Initial system state
Evolution of system state and test signals
Other parameters
Temporal resolution
Source of uncertainty
Suspension criteria / Stopping criteria
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Experiment Specification
Experiment Specification | Instructions are provided as comments in the rows
ID
Reference to Test Specification
Title of Experiment
Research Infrastructure
Description
Diagram Reference
Experiment Realisation
Description
Diagram Reference
Experiment Setup
Description
Diagram Reference
Experimental Design and Justification
Description
Diagram Reference
Precision of equipment and measurement uncertainty
Storage of experiment data
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## TC1
Test Case | Instructions are provided as comments in the rows
ID
| Name of the Test Case | Verification of the reliability of a redundant system or algorithm (e.g. failover)
Version management
Author
Version
| Project | ERIGrid 2.0
| Date | 10/05/2020
Narrative
| Description | The aim of this test case is to assess and verify the reliability of failover systems in smart grids that relies on putting redundancy. Redundancy is mainly used for critical smart grid applications such as protection in substations. In general, the redundancy can be either for control systems (such as the SCADA controller), communication networks or network controller (such as SDN controller), or a redundancy in the sensors and actuators (CT/PTs, Merging units, Breakers). Specifically, this test case looks into the reliability of failover systems with a redundancy in the communication networks. The ICT support system/communication network may fail due various reasons for e.g., component (hardware) failures, environmental failures (such as weather disruption failing multiple components), a power outage, overloading of the network (capacity shortage) or cyber-attack. A fail-over system tries to quickly detect failures and switch to backup systems (smooth transition in the case of active standby systems) or it tries to recover the system after experiencing some performance glitch (the case of passive standby system). Unlike active backup systems, in the case of passive redundant systems, there can be small system down time until the backup system is powered on and takeover. The test case investigates the reliability of active or passive fail over systems to verify if these systems can meet the requirements (delays, packet loss or system down time) specified by the smart grid application considered or requirements set by the standards and protocols such as IEC 61850.
Diagram reference
Function(s) under Investigation (FuI)
| Description | - Exchange of data (measurement and control commands) through the communication network - Control functions on the local controllers / IEDs - Protection functions on the local controllers / IEDs
Diagram reference
Object under Investigation (OuI)
| Description | Communication Network (network devices, switches, network links), control devices or IEDs
Diagram reference
Domain under Investigation (DuI)
| Description | - Information & Communication System - Control system - Power system
Diagram reference
Purpose of Investigation (PoI)
| Description | - PoI#1: Characterization of the performance of fail-over systems with a varying degree of redundancy. - PoI#1.1: Characterization of the performance of fail-over systems with redundancy in the communication network. - PoI#1.2: Characterization of the performance of fail-over systems with redundancy in the controller/IED - PoI#2: Characterization of the redundant communication/control system for its vulnerability towards cyber attacks - PoI#3: Verification of the system level performance with standard requirements (if it complies with the minimum expected KPIs e.g., down time, packet loss or delay)
Diagram reference
System under Test (SuT)
| Description | - Communication network (Switches, routers, network links) - Sensors (voltage sensors, CT/PT basic control), Actuators (breakers, intelligent switches) - SCADA Controller (for e.g., FLISR, voltage control, monitoring functions) or local controllers/IEDs - Power transmission system (substations, transmission lines)
Diagram reference
Functions under Test (FuT)
| Description | - Capability of the communication network/ devices to facilitate data exchange between controllers/IEDs, sensors and actuators (breaker, disconnectors) - Control and Protection functions - Monitoring capability of sensors (devices such as Merging units, PMUs) - Actuator (breaker, disconnector) functions
Diagram reference
| Test criteria (TCR) | - Run the system without introducing faults, and measure the communication network's performance during the normal operating condition… - Introduce a fault and measure the communication network performance degradation right after a failure/fault occur/injected. - Calculate and obtain the overall system performance (availability, reliability).
| Target Metrics (TM) | 1. End to end delay, packet loss - During a normal operating condition - After introducing a fault 1. Up time, down time, availability and reliability - After introducing a fault
| Variability Attributes (VA) | - Redundancy type and degree (active-active, active-standby, active-inactive) - Number of simultaneous (component) failures - Communication network traffic situation (background traffic) - Communication topology - Failure type - Cascading (from PS to CS) - Hardware - Software
| Quality Attributes (QA) | Pass: End to end delay (average, maximum) and packet loss are within the maximum limit or threshold values set by specifications on standard communication protocol or the smart grid application (such as protection) considered. OR, the availability, reliability measures are within the limit on the specification requirement set by system administrator. - Packet loss > T, where T is a threshold value set according to the application (protection) type considered. - Packet delay larger than D ms, where D is the delay tolerance which depend on the application (protection) type considered. The delay tolerance varies from 1 ms (for bus bar protection), 4 to 8 ms (for other type of protection schemes) up to 800 ms for IED to SCADA communication. Fail: If the measured metrics (delay, packet loss, availability, or reliability) exceeds the threshold values.
Qualification Strategy
Description
| Diagram reference | image1.png
Diagrams
| Diagram id | image1.png
| Diagram name | image1.png
| Diagram URI type | image
| Diagram URI value | image1.png

## TC23.1
Test Specification | Instructions are provided as comments in the rows
| ID | TC23.1
| Reference to Test Case | TC23
| Title of Test | Verification of the reliability of Substation Automation Systems (SASs) with redundancy in the communication network
Test Rationale
| Description | With the use of IEC 61850 standard, substations are nowadays becoming digitized and automated with digital relays/IEDs and a LAN based communication network for connecting these IEDs. Failure of the communication, even for the few milliseconds, may jeopardize critical functions such as protection and lead to catastrophic effects within or beyond the substation impacting the operation of grid. New redundant architectures, notably parallel redundancy protocol (PRP) and high High-Availability Seamless Redundancy (HSR) from IEC 62439-3, have been used to increase the reliability of IEC 61850 LAN based substation automation communication networks [1]. PRP provides high reliability through two independent LAN networks. The PRP enabled nodes are connected to these two isolated networks, which operate in parallel as shown below in Fig. 1 below. Frames are duplicated in the source and are sent over both networks; the destination PRP enabled node receives packets from the first network and accepts it, if it is correct, and then the copy from the second network will be discarded as duplicate. HSR operation is similar to PRP but HSR uses a single LAN with a ring topology and it uses two independent paths (clockwise and counterclockwise). Both architectures aim to provide an ideal “zero recovery time” with no packet loss. This test aims to investigate the reliability of these two recent redundant communication networks in substation automation. [1] International Electrotechnical Commission [2] S. Kumar, N. Das and S. Islam, "High performance communication redundancy in a digital substation based on IEC 62439-3 with a station bus configuration," 2015 Australasian Universities Power Engineering Conference (AUPEC), 2015, pp. 1-5, doi: 10.1109/AUPEC.2015.7324838.
Diagram Reference
Specific Test System
| Description | The specific test system consists of a real-time grid simulator, protection IEDS, Ethernet switches (x2), communication cables (x2). The real-time simulator is used to model the power system dynamics as well as some IED functions such as Merging unit (generating sampled values), circuit breaker functionality. The physical IEDs (for protection) will be connected to the real-time simulator through the two redundant communication networks in a C-HIL setup. Fig. 1: PRP Network Topology Fig. 2: HSR Network Topology
| Diagram Reference | image2.png; image3.png
| Target measures | - End to end delay and packet loss of IEC 61850 GOOSE and sampled value (SV) messages after the introduction of fault. - Availability and Mission reliability (ability to continually deliver service) of the communication network after the introduction fault.
| Input and output parameters | Input parameters: - Failure type - Failure rate of components - Repair rate of components - Communication network topology - Background traffic rate - Degree of redundancy Output parameters: - Maximum packet delay - Packet loss - Time duration of service interruption
Test Design
| Description | The test design is as follows. 1. System starts with normal operating conditions, no fault and there will be a normal GOOSE and SV stream (every 10 ms and 0.25 ms respectively) 1. Add some background traffic to the ethernet switches accounting for traffic from other IEDs or other devices in the substation. 1. Introduce faults in the system. This could be: 1. Failure in the communication network 1. OR, simultaneous failure in the communication network and the power system 1. During a failure in the communication network, the fail-over algorithm is activated and the system switches to the backup network with the redundant switches and network links. 1. If there is also a failure in the power system right before or after the failure of the communication system failure, it will also change the GOOSE traffic behavior (burst of GOOSE messages will be transmitted). 1. Collect the target measurements/metrics 1. end to end delay of GOOSE and SV streams between the IEDs and the virtual devices (MUs) in the Opal RT. 1. Down time of the communication between the IEDs and virtual MUs (if any) 1. Repeat these steps by varying the failure scenarios, background traffic, redundancy type and degree.
Diagram Reference
| Initial system state | Normal system state where there is no failure in the power and communication system. There will be a normal GOOSE (status update) between IEDs (also between IED and breakers), and SV streams from OPAL virtual MUs to the physical IEDs.
| Evolution of system state and test signals | 1. Initial state where there is no failure in the system (Normal GOOSE and SV streams) 1. Failure of network components and/or the power system occur. 1. The GOOSE and SV traffic pattern will change (for power system failures). The IEDs will send burst of GOOSE messages for a certain duration to make sure that faults are cleared on time. 1. When the IEDs or the PRP enabled ethernet switches detect a failure on the primary communication path (network), a fail-over function will be activated (in response to failure in the communication system) 1. The IEDs start to accept GOOSE and SV packets coming through the secondary path (network). 1. GOOSE data rate will return to the normal rate. 1. After a recovery of failed nodes (the communication network), IEDs and PRP enabled ethernet switches will revert back to accepting packets from the primary communication network.
| Other parameters | - Temporal order of contingency events - ICT failure causes PS fault - PS fault causes ICT failure - PS fault and ICT failure coincident
| Temporal resolution | 100 us
| Source of uncertainty | Background traffic data rate, configuration of the communication network (ethernet switches), Network devices or IED's capability to support the PRP/HSR architectures.
| Suspension criteria / Stopping criteria | Exceeding of quality attributes: - Communication is down for 200 milliseconds (protection related applications) or 3 second for SCADA- IED communication.
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
| Diagram id | image2.png | image3.png
| Diagram name | image2.png | image3.png
| Diagram URI type | image | image
| Diagram URI value | image2.png | image3.png