## HTD Template Information
Version | V1.3
Mandatory: All the cells in Column C in yellow have to be completed mandatorily.
Optional: The cells in blue are for multiple objects, that can be completed when needed.

## Test Case
Test Case | Instructions are provided as comments in the rows
ID
Name of the Test Case
Version management
Author
Version
Project
Date
Narrative
Description
Diagram reference
Function(s) under Investigation (FuI)
Description
Diagram reference
Object under Investigation (OuI)
Description
Diagram reference
Domain under Investigation (DuI)
Description
Diagram reference
Purpose of Investigation (PoI)
Description
Diagram reference
System under Test (SuT)
Description
Diagram reference
Functions under Test (FuT)
Description
Diagram reference
Test criteria (TCR)
Target Metrics (TM)
Variability Attributes (VA)
Quality Attributes (QA)
Qualification Strategy
Description
Diagram reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Test Specification
Test Specification | Instructions are provided as comments in the rows
ID
Reference to Test Case
Title of Test
Test Rationale
Description
Diagram Reference
Specific Test System
Description
Diagram Reference
Target measures
Input and output parameters
Test Design
Description
Diagram Reference
Initial system state
Evolution of system state and test signals
Other parameters
Temporal resolution
Source of uncertainty
Suspension criteria / Stopping criteria
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Experiment Specification
Experiment Specification | Instructions are provided as comments in the rows
ID
Reference to Test Specification
Title of Experiment
Research Infrastructure
Description
Diagram Reference
Experiment Realisation
Description
Diagram Reference
Experiment Setup
Description
Diagram Reference
Experimental Design and Justification
Description
Diagram Reference
Precision of equipment and measurement uncertainty
Storage of experiment data
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## 24
Test Case | Instructions are provided as comments in the rows
| ID | 24
| Name of the Test Case | Interoperability testing and validation in the activation chain of flexibility-related events in a local distribution network
Version management
| Author | Dimitrios Thomas, Petra Raussi, Vetrivel S. Rajkumar, Jawad Kazmi
Version
| Project | ERIGrid 2.0
| Date | 19/4/2021
Narrative
| Description | Smart grid interoperability is a main enabling facet of electricity technology developments. It comprises all parts of the smart grid, from generation to transmission and from distribution to consumption. Testing interoperability requires producing detailed test cases describing how smart grid components are intended to interact with each other. A systematic approach for developing smart grid interoperability tests may facilitate the dissemination of innovative solutions, the stability and resilience of the smart grid. The proposed Test Case is conducted following the JRC Smart Grid Interoperability methodology. The methodology is used mainly as a common framework for interoperability testing and consist of five stages; Use Case creation (UC), Basic Application Profile (BAP) creation, Basic Application Interoperability profile (BAIOP) creation, Design of Experiments (DoE), Testing and Analysis of Experiments (AE). Each stage allows the developer to select certain features then used in the subsequent stage. During the completion of all stages, the developer can select relevant standards, their options, test beds with all qualified and test equipment as well their attributes or functions used during the testing. The proposed methodology summarizes a set of best practices the developer could follow to complete in a smooth way a smart grid interoperability test. Fig.1 A schematic overview of the JRC Interoperability testing methodology In this test case, we will investigate through the interoperability validation tests, the interaction and information exchange between the involved actors for a flexibility activation event. This event will be triggered by a local node voltage disturbance and followed by a consequent flexibility request. To this end, we will analyze voltage restoration level, time and control.
| Diagram reference | TC24_Narrative.png
Function(s) under Investigation (FuI)
| Description | Voltage restore, activation and restoration time for interoperability profiles (BAIOP), validate the interfaces between the actors involved in the flexibility activation chain, impact to the grid. In this use case, we will analyze the performance of the “voltage restoration” function, after a voltage disturbance occurs in the power grid when different system variables (input factors) are considered and changed. The performance of this function is assessed an interoperability point of view, where different system variables (input factors) potentially affecting the system performance are considered and their effect on the system response is analysed. A reference grid model will be used (JRA1.1?).
Diagram reference
Object under Investigation (OuI)
| Description | The actual components and equipment under testing, e.g. communication infrastructure categorized by its technology (cable, Fiber, local Etherent, xDSL, etc.), controllers (e.g., RTU and Flexibility run in single-boards computers like Raspberry Pi), etc.
Diagram reference
Domain under Investigation (DuI)
| Description | - Communication/ICT/Control - Electrical Power System
Diagram reference
Purpose of Investigation (PoI)
| Description | Pol#1: Evaluate the interoperability between the involved actors and the different components in the system (flexibility provider, requester, other intermediates). Validate the interfaces along with specific communication technologies. Pol#2: Assess the restoration time and the level of the restored voltage among the different interface profiles
Diagram reference
System under Test (SuT)
| Description | - Lower bound communication architecture: from the DSO to the Device through a Remote Terminal Unit (RTU) à two communication links: DSO ↔ RTU and RTU ↔ Device - Distribution system (lines, transformers, etc.): power distribution network (MV/LV) / LV distribution feeder
Diagram reference
Functions under Test (FuT)
| Description | In-focus functions: Voltage restore (including restoration time), interoperability testing validation of the selected interfaces, real time simulator for the LV distribution benchmark network Emulated functions: ICT network emulator- communication network emulation, Controlling functions of the systems (e.g., DSO ↔ RTU and RTU ↔ Device) Actuation functions: Flexibility signal (demand response) to manage voltage disturbance event in a system node Observer functions: SCADA monitoring system to detect voltage deviations and instruct the RTU for the activation of the selected flexibility source available in the system
Diagram reference
| Test criteria (TCR) | - Safe and robust voltage for all nodes - Restore (in real time) of voltage to acceptable levels (0.95 pu < voltage < 1.05 pu) for the node the disturbance takes place - Restoration time for voltage testing the communication interfaces - Effectiveness of flexibility service activation patterns - Communication functionality, configuration and interoperability validation for all the tested interfaces
| Target Metrics (TM) | - The value of the voltage measured at node 𝑖 after the flexibility (located at the same node) is activated in the attempt of restoring the voltage within the allowed DSO-specific voltage range - The time the system took in order to restore the voltage at node 𝑖
| Variability Attributes (VA) | The admitted voltage deviation, which is the maximum allowed value from which the node voltage, in percentage, can deviate with respect to the reference voltage. This parameter is meant to be a DSO-oriented factor, and the influence of its variability on the system outputs (together with that of the other considered input factors) is studied.
| Quality Attributes (QA) | - Power quality standard EN50160 - All node voltages within the specified limit (+ or -10%) - System restoration time
Qualification Strategy
| Description | Both PoI#1 and PoI#2 are met with Test Specification 24.01. The overall interoperability evaluation for the test will be in the form of a final “pass/fail” form. For PoI#2, the time that the system needs to activate the voltage support mechanism and successfully restore the voltage to acceptable levels will be evaluated. It should be also mentioned that although both PoI can be met by TS 24.01, multiple interfaces (each one corresponding to a different BAIOP) depending on the selected telecommunication technology will be tested for the two communication links under consideration (DSO ↔ RTU and RTU ↔ Device). These will result in multiple experiment specifications.
Diagram reference
Diagrams
| Diagram id | TC24_Narrative.png
| Diagram name | TC24_Narrative.png
| Diagram URI type | image
| Diagram URI value | TC24_Narrative.png

## 24.01
Test Specification | Instructions are provided as comments in the rows
| ID | 24.01
| Reference to Test Case | Interoperability testing and validation in the activation chain of flexibility-related events in a local distribution network
| Title of Test | Interoperability validation and evaluation of the activation chain to satisfy a DSO flexibility request as a response to a voltage disturbance event at a specific grid node.
Test Rationale
| Description | The aim is to investigate through the interoperability validation tests, the interaction and information exchange between the involved actors for a flexibility activation event. This event will be triggered by a local node voltage disturbance (functional disruption) and followed by a consequent flexibility request.
Diagram Reference
Specific Test System
Description
Diagram Reference
| Target measures | In the system under test, the interoperability test will be in the simple “pass/fail” form. The time the system requires to restore the voltage back to the desirable deviation levels is evaluated, i.e., the time that the system takes to respond to the voltage support mechanism after a disturbance in the power grid. If this time = ∞ --> fail, else --> pass
| Input and output parameters | - Internal RTU time delay - Reference Voltage - Admitted Voltage Deviation - Time required for Flex to activate - Available flexibility capacity - Maximum activation time for flexibility
Test Design
| Description | A simulation period of X minutes long, during which a functional disruption is introduced in the system. This disruption causes a voltage disturbance and results in a flexibility activation request to restore the system back to acceptable conditions. The connection and communication between all the involved actors in the activation chain is evaluated under an interoperability point of view.
Diagram Reference
| Initial system state | Initially the system service is operating “as usual”. The grid loads are at their nominal values and the grid is functioning without disruptions. As far as the communication is concerned, we assume that the communication links between the various actors are 100% reliable.
| Evolution of system state and test signals | The networked is continuously monitored by the SCADA. A voltage disruption (disturbance) is introduced at a specific node. The system (through the DSO) asks for flexibility so as to restore the voltage in a reasonable time period. The interconnection between the whole activation chain and all necessary actors is studied and assessed under an interoperability point of view.
Other parameters
| Temporal resolution | To be determined
| Source of uncertainty | Only a deterministic type of disruption event is introduced.
| Suspension criteria / Stopping criteria | 30 minutes or permanent loss of communication and/or grid connection
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value