## HTD Template Information
Version | V1.3
Mandatory: All the cells in Column C in yellow have to be completed mandatorily.
Optional: The cells in blue are for multiple objects, that can be completed when needed.

## Test Case
Test Case | Instructions are provided as comments in the rows
ID
Name of the Test Case
Version management
Author
Version
Project
Date
Narrative
Description
Diagram reference
Function(s) under Investigation (FuI)
Description
Diagram reference
Object under Investigation (OuI)
Description
Diagram reference
Domain under Investigation (DuI)
Description
Diagram reference
Purpose of Investigation (PoI)
Description
Diagram reference
System under Test (SuT)
Description
Diagram reference
Functions under Test (FuT)
Description
Diagram reference
Test criteria (TCR)
Target Metrics (TM)
Variability Attributes (VA)
Quality Attributes (QA)
Qualification Strategy
Description
Diagram reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Test Specification
Test Specification | Instructions are provided as comments in the rows
ID
Reference to Test Case
Title of Test
Test Rationale
Description
Diagram Reference
Specific Test System
Description
Diagram Reference
Target measures
Input and output parameters
Test Design
Description
Diagram Reference
Initial system state
Evolution of system state and test signals
Other parameters
Temporal resolution
Source of uncertainty
Suspension criteria / Stopping criteria
Mapping to Research Infrastructure
Description
Diagram Reference
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## Experiment Specification
Experiment Specification | Instructions are provided as comments in the rows
ID
Reference to Test Specification
Title of Experiment
Research Infrastructure
Description
Diagram Reference
Experiment Realisation
Description
Diagram Reference
Experiment Setup
Description
Diagram Reference
Experimental Design and Justification
Description
Diagram Reference
Precision of equipment and measurement uncertainty
Storage of experiment data
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value

## 25
Test Case | Instructions are provided as comments in the rows
| ID | 25
| Name of the Test Case | Cyber Security of Digital Substations and Impact Analysis
Version management
| Author | Petra Raussi (VTT), Vetrivel Subramaniam Rajkumar (TUD)
| Version | 1
| Project | ERIGrid 2.0
| Date | 19/4/2021
Narrative
| Description | The energy transition towards a carbon neutral and clean energy system requires increased power grid digitalization. This is seen as the most cost-effective path in developing smart grids. An essential part of any functional power system are substations; thus, their digitalization is crucial. While the digitalization of power system brings several benefits from cost savings to more optimized operations and investments, it also raises concerns related to cybersecurity. To ensure safe and resilient operation of digital substations even in the case of cyber attacks or incidents, it is necessary to investigate their cyber resilience. This can aid in impact analysis of cyber attacks on digital substations, and help to gain deeper understanding of which components must be most secured
Diagram reference
Function(s) under Investigation (FuI)
| Description | - Grid stability and operation when impacted by cyber-attacks/incidents - Cyber resilience of digital substations
Diagram reference
Object under Investigation (OuI)
| Description | Digital substation components and communication systems: - substation bays (busbars, disconnectors, circuit breakers, current and voltage transformers), - merging units, - Ethernet switches, - HMIs, - time servers, - IEDs, - centralized protection and control units, - station control systems, - process bus, and - communication gateways.
Diagram reference
Domain under Investigation (DuI)
| Description | - ICT - Electrical power system
Diagram reference
Purpose of Investigation (PoI)
| Description | To carry out impact analysis of cyber-physical events on digital substations and quantify impact on grid operations.
Diagram reference
System under Test (SuT)
| Description | In power system domain: digital substation including substation bays, merging units, Ethernet switches, HMIs, time servers and IEDs centralised protection and control units, station control systems, etc. A substation bay comprises of busbars, disconnectors, circuit breakers, current and voltage transformers, etc. In ICT domain: communication within the substation via local operating networks (process bus) at bay level using communication protocols such as IEC 61850 and LAN at the station level for communication with the control centre via dedicated communication gateway and protocols such as IEC 104 and DNP3. Hence, to realize this test case, the following components are required: - Real-time grid simulator such as RTDS or OPAL-RT that supports Hardware-in-Loop (HIL) studies - Substation network elements: 1. At least one ethernet switch and time server. At least two or more physical IEC 61850 capable IEDs 1. RTUs, MUs, other HIL devices - A dedicated communication network emulator to model disturbances/cyber attacks The testing involves interfacing the real-time grid simulator with all hardware components in a HIL setup to mimic a digital substation. Furthermore, the real-time grid simulator also needs to be interfaced with the network emulator to model and input communication related effects such as latency, packet loss, loss of service, etc. Source: Centralized Protection and Control. ABB Whitepaper, 2020. Link:
| Diagram reference | TC25_System_under_Test.png
Functions under Test (FuT)
| Description | - Capability of test setup to exchange data using IEC 61850 and IEC 60870-5-104 - Automation and protection functionality realized by OuI - Behaviour and performance of substation, when subjected to specific cyber attacks/threats
Diagram reference
| Test criteria (TCR) | - Equipment response and performance under normal operating conditions - Equipment response and performance when subjected to specific cyber attacks/threats. - Impact of particular attack/threat on overall system performance
| Target Metrics (TM) | Cyber security performance and resilience testing - This TC assumes that the substation is conformant to IEC 62351-6 and tests its implementation for resiliency. - For e.g., through Denial-of-Service attacks, malformed authentication codes, etc. Impact on Power system - KPIs: loss of load, voltage deviations, frequency fluctuations, etc.
| Variability Attributes (VA) | - Overall substation configuration and topology - Network emulator characteristics - Redundancy (N-1, N-2…. N-k): Number of components or communication links which can fail before system operation is at risk - Topology and type of simulated power system (transmission vs distribution)
| Quality Attributes (QA) | - System performance under cyber attacks - Pass: all KPIs within maximum limits/bounds - Fail: at least one KPI maximum limits
Qualification Strategy
| Description | The PoI are mainly addressed by characterizing and verifying the impact of cyber attacks in digital substations on grid operations. This can be achieved by determining how substation functionality and thereby power system stability and operations are directly affected by cyber-physical attacks.
Diagram reference
Diagrams
| Diagram id | TC25_System_under_Test.png
| Diagram name | TC25_System_under_Test.png
| Diagram URI type | image
| Diagram URI value | TC25_System_under_Test.png

## TC25.TS1
Test Specification | Instructions are provided as comments in the rows
| ID | TC25.TS1
| Reference to Test Case | TC25
| Title of Test | Impact analysis of Denial-of-Service (DoS) attack in a digital substation
Test Rationale
| Description | A digital substation is realised by the IEC 61850 standard which mandates a common Ethernet based communication infrastructure within a substation. This experiment seeks to analyse the impact of a DoS attack that successfully compromises the substation communication infrastructure. This may lead to delayed or loss of trip, block commands, thereby directly impacting grid operations.
Diagram Reference
Specific Test System
| Description | The test system comprises of a real-time grid simulator, at least one Ethernet switch, and multiple IEC 61850 compliant devices interconnected in a HIL setup. (See SuT for further information)
| Diagram Reference | TS25.01_Specific_Test_System.png
| Target measures | - KPIs: loss of load, voltage deviations, frequency fluctuations on simulated system under a DoS attack - Time taken and quality of service for IEC 61850 based communication under a DoS attack
| Input and output parameters | Input parameters: - Type of power system simulated - Network topology of substation - Protection schemes applied through the relays - Fault type and duration - Type of attack: DoS Output parameters: - KPIs: loss of load, voltage deviations, frequency fluctuations on simulated system under a DoS attack - Avg time for intra substation communication and communication quality of service (jitter, packet loss, latency, throughput, availability)
Test Design
| Description | The test is a HIL experiment as described in the SuT and specific test system. The test consists of a reference test for the baseline measurements and repeat of this test with the DoS attack. The test design is as follows: 1. Start the system with all devices functioning as required and the system is stabilized. 1. Run a test simulation with a short-circuit or fault condition at location monitored by relay. 1. Note that the appropriate relay communicates trip signal via IEC 61850 GOOSE message. Note this time as reference time T1. 1. Circuit breaker is opened, and the fault is cleared. 1. Carry out DoS attack via external emulator/device to target specific IED/relay. 1. Repeat steps 2 to 3 and note the new time T2. 1. Quantify impact of attack through KPIs and note down targeted device. 1. Repeat for additional target devices at different locations to identify most critical digital asset.
Diagram Reference
| Initial system state | - All devices are ON and running - Real-time grid simulator can send and receive messages to and from the hardware devices - IEDs receive messages from the real-time grid simulator
| Evolution of system state and test signals | Successful recording of KPIs for each targeted device. The fault event generated by the real-time grid simulator has predeterminate fault duration and wait time. The DoS attack operates independently of the HIL experiment sequence and can occur at any moment of time in the sequence.
| Other parameters | N/A
| Temporal resolution | Order of tens of seconds
| Source of uncertainty | Configuration of HIL test setup, quality of time synchronization.
| Suspension criteria / Stopping criteria | Suspension criteria: Errors in devices/misconfiguration Stopping criteria: the experiment can be concluded when the KPIs for various target devices are noted. Alternatively, if the attack causes cascading effects or a blackout, it can be stopped.
Mapping to Research Infrastructure
| Description | Trying known cyber-attack malware, etc. on the digital substation and seeing the impacts of that, which components should be the most heavily guarded. What are the impacts of cyber-attack on the power system, in which components are influenced?
Diagram Reference
Diagrams
| Diagram id | image2.png
| Diagram name | image2.png
| Diagram URI type | image
| Diagram URI value | image2.png

## ##.##.##
Experiment Specification | Instructions are provided as comments in the rows
| ID | ##.##.##
Reference to Test Specification
Title of Experiment
Research Infrastructure
Description
Diagram Reference
Experiment Realisation
Description
Diagram Reference
Experiment Setup
Description
Diagram Reference
Experimental Design and Justification
Description
Diagram Reference
Precision of equipment and measurement uncertainty
Storage of experiment data
Diagrams
Diagram id
Diagram name
Diagram URI type
Diagram URI value